## Table 2
RFP Reference: UHS/ENG/TENDER/021/2026 3rd June 2026 RFP Closing Date: 18th June 2026

## Table 3
No. | Description
1 | Conversion of Administration Area to OBG Ward

## Table 4
University Hospital Sharjah. (UHS) Management has decided to invite vendors for a Request for Proposal (RFP). You, as a vendor are requested to participate in the RFP process by submitting your offer to provide the services as described in this document.

## Table 5
The RFP should comply with the following terms & conditions:

## Table 6
1. The proposal shall be clear, informative & include as per the requirement described in the RFP. 2. The financial offer should be on your company letterhead containing the authorized signatory and must be sent to the attention of the Director of Finance, University Hospital Sharjah, PO Box 72772, Sharjah in a sealed document.

## Table 7
3. The price quoted is as mentioned in the technical requirement listed below (RFP) to UHS.

## Table 8
4. All deliveries should be made for the ordered quantity in full, without partial shipments, to our Main Warehouse, located in UHS vicinity or as specified on the Purchase Order/ Contract. Failure to comply with the agreed delivery schedule or any shortfall in quantity may result in penalties or contract termination, as per the Purchase Agreement Terms and Conditions.

## Table 9
5. As a part of the RFP document, the Vendors are requested to provide their valid Trade License, Name, and Designation of the Managing Director/General Manager/Sr. Manager having the authority to bind their company for the business relationship. Also, the vendors are required the provide licenses, certificate confirming that the vendor is legalized to operate the proposed business activity. As well as the following documents:

## Table 10
a) Valid Trade License b) Updated Company Profile c) Tax Registration Certificate (TRN) d) Full Company Address & Contact Details e) Memorandum of Association (MOA) and Power of Attorney (POA) for authorized signatory (if applicable) f) An official Authorization Letter/Agency Certificate, confirming the vendor's legal authorization to supply the specified items on behalf of the manufacturer or principal company. g) Any additional approvals or compliance documents mandated by government authorities for the supply of the specified equipment. h) Non-Liability Letter and Legal Clearance Confirmation. i) Insurance Policies (General Liability, Professional Indemnity, etc.).

## Table 12
j) Declaration of No Ongoing Legal Disputes. k) Vendor Code of Conduct Acknowledgment. 6. Standard payment terms are 90 days from the date of completion of delivery of supplies/ services or as specifically agreed in purchase contract/ agreement.

## Table 13
7. Any delays or non-conformance may result in the termination of Services agreement and/or imposition of penalty for delayed services as per the Services Agreement terms and conditions. A performance bond may be required to ensure commitment to the agreed timelines and quality standards.

## Table 14
8. The proposed services shall be evaluated & approved by UHS’s before confirmation. Once the agreement is signed off, the services will have to correspond to the required services with specific time-frame, and as originally proposed, agreed and any deviations shall be considered a breach of service contract/agreement.

## Table 15
9. The specified brand and manufacturer must remain unchanged throughout the contract period unless otherwise approved by UHS in writing.

## Table 16
10. UHS will be constantly evaluating the compliance of Contract/Agreement Terms and consistency in performance of the services throughout the duration of the agreement.

## Table 17
11. Vendors are required to submit regular progress reports at agreed intervals detailing progress, challenges, and actions to address any delays or issues. Should Vendors not meet the requirements of UHS, UHS reserves the right to terminate the agreement if the vendor is not able to rectify during the time allotted by UHS’s representative.

## Table 18
12. Vendor Contact details (landline, mobile, emails) of the authorized representatives should be mentioned.

## Table 19
13. Tenders should be submitted in two sealed envelopes and submitted to the Administration Office Finance Department- UHS:

## Table 20
a. The Technical Specification details (PLEASE DO NOT INDICATE ANY FINANCIAL VALUE IN THIS). If requested for additional clarifications and details these need to be submitted to (Administration Office Finance Department- UHS).

## Table 21
i. The offer should must conform to the RFP Document as per the attachment. ii. The offer shall be submitted (hard copy and soft copy saved in USB). iii. Reference Project/Hospital where similar work was performed.

## Table 22
b. The Financial Offer addressed to UHS’s Director of Finance, with tender reference.

## Table 23
All above documents should be submitted before the tender expiry date, all documents submitted after the expiry date will not be accepted.

## Table 24
14. UHS shall have no obligation to accept any tender proposal submitted by any vendor. UHS may at its sole discretion and without providing any reason, accept or reject any or all

## Table 26
proposals, in whole or in party. Such rejection shall not give rise to any claim, liability, or cause of action of any king by the vendor against UHS. 15. Submission of a tender proposal shall not create and agreement, legal or other relationship between the vendor and UHS. No vendor shall acquire any rights, interests, or claims against UHS by submitting a proposal, participating in the tender process or relying on any communications related to the tender. 16. In the event UHS accepts a tender proposal of a vendor, the parties agree any such tender award will be subject to a Services Agreement and separate agreement outlining the specific terms and conditions of the project and services agreed. 17. All costs, expenses or losses incurred by the vendor in connection with the preparation, submission of presentation of its proposal shall be borne sole by the vendor. UHS shall have no liability, under any circumstances to reimburse, compensate or indemnify the vendor whether in part or in whole for such costs or expenses. 18. The vendors acknowledge and agree that they have not relied on any statement, representation, warranty, or promise made by UHS, whether oral or written, in preparing their tender proposal and all decisions and judgements regarding the submission of their proposal are made at their own discretion and risk. 19. UHS may at any time without liability, amend, suspend, or withdraw the tender invitation in whole or in part. UHS may also request additional information, clarifications or documents from any vendor and may reject any proposal that is incomplete, unclear or does not comply with the tender requirements as outlined in this document. 20. Quality, Price, and sale services are combined parameters for tender evaluation. Once a vendor has been selected, a negotiation period will follow to allow both parties to review the agreement terms thoroughly. This will ensure that all deliverables, KPIs, and expectations are clearly outlined before the final agreement is signed. 21. . Vendors must submit a risk management plan, identifying potential risks to the project, such as security and confidentiality breaches, system failures, and disruptions to delivery schedules. Vendors should outline how they intend to address these risks, including their disaster recovery and business continuity plans. 22. Vendors are encouraged to adhere to ethical practices and sustainability standards in their operations. This includes providing energy-efficient equipment and adopting environmentally friendly practices in their supply chain and delivery. 23. The Vendor, its employees, its subsidiaries, and everyone who has a direct or indirect relationship with implementing and securing the works and Services included within the scope of this tender, shall be obligated to inform UHS and disclose in writing any case of conflict of interest or any private interest that has arisen, will arise, or may arise. For any transaction related to the activities of UHS, in accordance with UHS policies. 24. The vendor, its employees, and subsidiaries shall be obligated to maintain confidentiality of any data, drawings, documents, or information related to the tender - written or oral. Vendors must ensure that any data shared is protected by encryption standards and secure transfer protocols. Additionally, vendors are required to notify UHS of any data breaches immediately. Compliance with relevant data privacy regulations (e.g., GDPR, UAE Data Protection Law) is mandatory. This includes all dealings, affairs, or secrets related to UHS they may have encountered during the tender process. Vendors shall not be allowed to disclose any information related to the tender through any media outlet without obtaining prior written approval from UHS.

## Table 27
25. The copyright, rights and ownership of any documents, materials and information submitted by UHS within this tender is owned by UHS, and accordingly, these documents and materials

## Table 29
may not be copied, in whole or in part, or reproduced, distributed, made available to any third party, or used without obtaining prior written approval from UHS. If the vendor develops any custom software or systems for UHS as part of this tender, UHS will retain ownership of the intellectual property or have clear licensing terms for its continued use. All documents submitted by the UHS in connection with the request for proposals shall be returned upon request without any copies being retained by the bidder or any other person.

## Table 30
26. The vendors shall indemnify, defend and hold harmless UHS, its officers, employees and agents from and against any and all claims, liabilities, losses, damage costs, or expenses arising out of or in connection with:

## Table 31
a. the vendors participation in the tender process b. any errors, omissions, misrepresentations or inaccuracies in the proposal c. any breach of the vendors’ obligations under this tender invitation

## Table 32
27. To the maximum extent permitted by law, UHS expressly excludes any liability for: a. Any direct, indirect, incidental, consequential or special losses b. Loss of profits, revenue, goodwill or business opportunities c. Any claims by third parties arising from a vendor’s proposal d. Any loss or damage caused by errors, omissions or delays in the tender process 28. This tender invitation and all matters relating to it shall be governed by any construed in accordance with the laws of the United Arab Emirates. The competent courts of Sharjah, United Arab Emirates shall have exclusive jurisdiction over any disputes arising from or in connection with this tender. 29. This document and clauses therein constitute the entire understanding between UHS and any vendor regarding liability, proposal submission, and the tender process. No other communication, agreement or understanding, whether oral or written shall be deemed to modify, supersede, or expand these clauses.

## Table 33
University Hospital Sharjah

## Table 35
Request for proposal RFP and Scope Of work for Admin Block conversion to OBG Ward.

## Table 36
Total Covered area to be renovated is =1300 SQM The current area application is Administration Area. The proposed Area Application will be Female General Ward.

## Table 37
1. Scope of Work The scope includes the complete renovation and conversion of an existing 1300 sqm administration area into a fully complied female general ward. The works shall include:  Architectural modifications (Internal Only)  MEP (Mechanical, Electrical, Plumbing) works  Medical gas systems  Fire safety systems  IT and nurse call systems  Interior finishes  Furniture, Fixtures & Equipment (FF&E)  Compliance with infection control and patient safety standards

## Table 38
2. Design and Planning Requirements  Functional Planning Unit (FPU): Inpatient Unit (Medical)  Room Types: Patient rooms (single), patient isolation room, nurse stations, treatment rooms, services such as clean/dirty utility, staff areas, storage, separated directors offices, and meeting rooms as per design.  Minimum Room Sizes: As per Health Authority Room Data Sheets (RDS) and Room Layout Sheets (RLS)  Accessibility: Compliance with Health authority Healthcare Facility Guidelines ( Part C – Access, Mobility, OH&S)  Infection Control: As per Health Authority Healthcare Facility Guidelines Part D – Infection Control Guidelines  Engineering Services: As per Health Authority Healthcare Facility Guidelines Part E – Engineering Guidelines

## Table 39
3. Regulatory Compliance  All work must comply with:  Health Authority Healthcare Facility Guidelines (Parts A–F)  Sharjah Civil Defense (DCD) fire safety regulations  Sharjah Municipality building codes  SEWA and Etisalat/DU requirements for utilities and IT

## Table 40
4. Deliverables  Detailed architectural and engineering drawings  Detailed BOQ  Room data sheets and layouts  Medical equipment layout and specifications  Fire and life safety plans  Phasing and implementation schedule RFP (request for Proposal)

## Table 41
Space Standards and Components:

## Table 42
In new facility, the maximum room capacity shall be one patient per room. Minimum dimensions, excluding such items as ensuites, built-in robes, alcoves, lockers, entrance lobbies and floor mounted mechanical equipment shall be as follows:

## Table 43
Room Type | Minimum Width | Minimum Length | Minimum Area
SINGLE BEDROOM | 3800 mm | 3960 mm | 18m2

## Table 45
These spaces should accommodate comfortable furniture for one or two family members or carers without blocking staff member access to patients. Minimum room dimensions are based on overall bed dimensions (buffer to buffer) of 2200mm long x 1050mm wide. Minor encroachments including columns and hand basins that do not interfere with functions may be ignored when determining space requirements

## Table 46
shall be followed exactly

## Table 47
The AutoCad proposed layout file attached with this proposal rooms, and offices. | including all designated areas,

## Table 48
Support Areas

## Table 49
Support Areas include: • housekeeping • Equipment bays • Clean Utility  Dirty Utility and Disposal Rooms • Pantries • Lockers room • Storage rooms

## Table 50
Bed Spacing / Clearances:

## Table 51
All patient beds must comply with standard components for fittings, furniture, mechanical and electrical services and nurse call systems including the clearances that they imply. In bedrooms there shall be a clearance of 1200 mm available at the foot of each bed to allow for easy movement of equipment and beds.

## Table 52
Accessibility:

## Table 53
Bedrooms and ensuites should comply with accessibility requirements in line with regional and international standards; including NFPA. Accessible bedrooms and ensuites should enable normal activity for wheelchair dependent patients, as opposed to patients who are in a wheelchair because of their hospitalization.

## Table 54
Doors:

## Table 55
Door openings to inpatient bedrooms shall have a minimum of 1200mm clear opening to allow for easy movement of beds and equipment.

## Table 56
Safety and Security:

## Table 57
The facility, furniture, fittings and equipment must be designed and constructed in such a way that all users of the facility are not exposed to avoidable risks of injury.

## Table 58
Drug Storage:

## Table 59
All drugs should be managed by the responsible nurses via a Medication Room. Optionally Medication Room may be combined with a Clean Utility room as long as the requirements of both functions are accommodated Controlled or dangerous drugs must be kept in a secure cabinet within the Medication Room with alarm. A refrigerator, as required; to store restricted substances, it must be lockable or housed within a lockable storage area. Medication Room must have space for parking a medication trolley.

## Table 60
Finishes:

## Table 61
Finishes including building fabric, floor, wall and ceiling finishes, should be relaxing and noninstitutional as far as possible and shall be medical grade. The following additional factors should be considered in the selection of finishes: 1. acoustic properties 2. durability 3. ease of cleaning 4. infection control 5. fire safety 6. movement of equipment In areas where clinical observation is critical such as bedrooms and treatment areas, colour selected must not impede the accurate assessment of skin tones. Walls shall be painted with lead free paint.

## Table 63
Curtains / Blinds

## Table 64
Each room should have partial blackout facilities (blinds or lined curtains) to allow patients to rest during the daytime. Window curtains and privacy bed screens must be washable, fireproof and cleanly always maintained. Disposable bed screens may also be considered. If blinds are to be used instead of curtains, the following will apply: Vertical blinds and Holland blinds are preferred over horizontal blinds as they do not provide numerous surfaces for collecting dust. Horizontal blinds may be used within a double- glazed window assembly with a knob control on the bedroom side.

## Table 65
Building Services Requirements

## Table 66
1. Demolition work in compliance with the Hospital Infection control policy. 2. Civil and fit out works in compliance with the existing facility Specification Specially for the conversion wet area (Washroom, Housekeeping Room, etc.) 3. As per the site requirement, the coring and chipping in the RCC slab prior to proceed

## Table 67
scanning and structural

## Table 68
| analysis compliance | shall be done.
 Plumbing Scope of work (Dismantling and isolating the Area):

## Table 69
1. Dismantle existing plumbing services and fixtures, plug unnecessary connections, and extend plumbing to a new location as per the proposed layout to meet end-user requirements. Locate all existing plumbing services within the proposed Ward area. 2. Ensure the main water supply to the room is shut off to prevent any water leakage during the dismantling process. Securely plug all unnecessary plumbing connections to prevent any leaks. Ensure that all plugs are properly sealed and tested for leaks. 3. Install new piping and fixtures as per the proposed layout. Ensure all connections are secure and leak-free. 4. Test the newly installed plumbing services for proper functionality and leaks.

## Table 70
 Plumbing Scope of work (Supply and Installation)

## Table 71
The scope of work includes, but is not limited to, the supply and installation of the following: 1. Domestic Water Supply Piping:  Install cold and hot domestic water supply piping. 2. Auto Sink Mixer:  Supply and install auto sink mixers. 3. 55 cm Wash Basin:  Supply and install 55 cm wash basins at different locations as shown in drawing. 4. Drainage Piping:  Install drainage piping as required. 5. Scanning for Drainage Connection:  Perform scanning of the 1st floor lower level, and ground floor high level for drainage connections. 6. Core Cutting:  Conduct core cutting as per site requirements. 7. Floor Chipping for Drainage Piping:  Perform floor chipping for drainage piping as per site requirement. 8. Pressure and Leak Testing:  Conduct pressure and leak tests in accordance with standards. 9. Identification Stickers and Bends:  Provide and install identification stickers and bends as required. 10. As-Built Drawings:  Prepare and submit as-built drawings, incorporating existing services drawings.

## Table 72
HVAC Supply and Installation

## Table 73
Total Covered Area approximately = 1300 SQM Available Air flow from AHU 16 Recirculation Only = 11840 l/sec

## Table 74
The following requirements must be adhered too for Patient Room HVAC systems. As a minimum Patient room should be provided with temperature control (21-24°C), maximum 60% RH, with a 6 ACH SA/ 2 ACH OA. Each patient room should be provided with a thermostat linked with the existing BMS system (Honey well and Alerton) .

## Table 76
1. GI Ducting Installation:  Modification in the main supply and installation of new Heater batteries to achieve the required temperature. Installation of GI ducting for air distribution, including both modifications and new installations, as per site requirements in all the individual user areas. 2. Volume Control Dampers (VCDs) and Fire Dampers (FDs):  Supply and install VCDs and FDs as required for the project. 3. Mineral Wool Insulation:  Install mineral wool insulation as per hospital requirements for the proposed layout to ensure proper air distribution, adhering to ASHRAE standards. 4. Air Outlets ( Grill/Diffusers) :  Supply and install powder-coated Air Outlets ( Grill/Diffusers) as per approved RFC.

## Table 77
5. Heater Batteries:  Install, test, and commission heater batteries for the following areas:  Addition of heater Batteries with flow capacity as per requirement in every patient room as well individual user area. 6. LTHW Piping and Valve Package:  Supply and install low-temperature hot water (LTHW) piping and valve package for new heater battery (MS Pipe Schedule 40 or PPR recommended ). 7. Water and Air Balancing, Testing, and Commissioning:  Perform water and air balancing, testing, and commissioning for the renovated area. 8. Identification Stickers and Bends:  Provide and install identification stickers and bends as required. 9. As-Built Drawings:  Prepare and submit as-built drawings, incorporating existing services and structure drawings.

## Table 78
Scope of Work: BMS Control

## Table 79
1. The contractor shall include the supply of all items of control equipment such as valves and thermostats, and damper motors/actuators. The BMS contractor shall also include the off-loading, positioning, and fixing of all control panels. 2. Provide and commission BMS integrated thermostats in individual user area. 3. Start-Up Test and Validation:  Conduct start-up tests and validation of the BMS. 4. As-Built Composite Electric Diagrams:  Provide as-built composite electric diagrams showing interlocks between equipment furnished under this and other sections, and controls furnished herein. 5. Completion Reports:  Upon completion of work, submit reports of check-out and successful commissioning of the BMS.

## Table 80
Scope of Work: Central Medical Gas System Supply and Installation

## Table 81
Supply and install Bed Head unit Nos. 1 each patient room including Central Medical Gas (Medical Oxygen, Medical Air, and Vacuum) each patient room upon the drawing and sample approval from the end user. The system should be installed as per SHA Standards in proposed area. 1. Complete System Design and Installation:  This includes the complete detailed design, supply, erection, setting to work, testing, commissioning, and handing over of the medical gas pipeline systems to form a complete installation as scheduled and in accordance with the specifications and in full compliance with all relevant standards and the requirements of NFPA 99. 2. Testing Standards:  Medical gas installations shall be tested in accordance with NFPA 99, Health Technical Memorandum U.K. (HTM-02) standards for medical gases installation, and Euro Pharmacopoeia for medical gas quality. 3. Medical Grade Piping:  Install medical grade piping from the existing provision near the nurse station in the pediatric ward. 4. Future Connection and Isolation Valves:  Tap-up from the existing future connection and extend for future connection with a new set of isolation valves.

## Table 83
5. Pressure and Leak Testing:  Conduct pressure and leak tests in accordance with standards. 6. Identification Stickers and Bends:  Provide and install identification stickers and bends as required. 7. As-Built Drawings:  Prepare and submit as-built drawings, incorporating existing services drawings.

## Table 84
Electrical Scope of work

## Table 85
Power and lighting. 1. Electrical Power Design Drawing as per proposed layout. 2. As built Load schedule. 3. Provision for Normal /emergency /UPS power as per requirement of new load schedule. 4. Addition of DB and SMDB according to new load schedule in DB. 5. PVC and GI Conduit & cable pulling for the required power outlets and lighting as per new layout. 6. Lights of approved Lux shall be installed as per Clinical requirement with 50, 000 Hrs life span. 7. Cable tray and trunking to be provided as per the area requirement. 8. Earth strip be provided for all the mechanical containment and connected to main earthing system. 9. Provide detailed documentation of the cable installation, including as-built drawings, test reports, and compliance certificates.

## Table 86
Central Battery

## Table 87
1. In each separate area one light shall be connected to the Central Battery System via through SCM and SVAEL, along with programming and updating in easy check panel. 2. Civil Defense approved Exit Light shall be installed as per NFPA and Local Authority Standards. 3. Updating the Evacuation plane as per new proposed layout.

## Table 88
Fire Alarm System

## Table 89
1. Supply installation, testing and reprogramming of Fire alarm system and addition of Smoke detectors in proposed area as per NFPA and civil defense requirement.

## Table 90
Telephone Data

## Table 91
1. Cat 6 UTP Schinder Shall be provided for the telephone and data network. 2. Trunking and Containment, wiring, final fix testing and commissioning from point to IDF panel and patch panel shall be provided as per requirement. 3. Labeling shall be provided to all the telephone outlets.

## Table 92
Nurse Call System

## Table 93
Supply and installation of Nurse Call system along with Containment, wiring and final fix shall be installed and programmed as per existing make (Honeywell) including integration main system in proposed area.

## Table 94
MEP Material Specification

## Table 96
Low Temperature Hot Water Heater Battery

## Table 97
A low temperature hot water coil (LTHW) coil shall be provided to heat the supply air at each individual user area. The valve position shall be modulated when the normal operating period is signaled by the BMS and the supply fan is proven. Flexible Ducting 1. Flexible ducting shall be provided for connections between ductwork, terminal units, diffusers if required. It shall conform to the requirements of BS 476 Parts 6, 7 (class 1) & part 20 (15 minutes). 2. Maximum lengths shall be 1.5 meters, and all ducting shall be adequately supported to prevent oscillation and noise generation. 3. Flexible connections shall be kept as short as possible and shall be supported rigidly to prevent movement due to air flow. Ductwork Identification Markers 1. Comply with DW 144 for identification of ductwork. 2. Direction of flow markers shall be provided on all ductwork to identify the service and direction of flow. Markers shall be of triangular shape of 150 mm length of side and point in the direction of flow. 3. Direction of flow markers shall be provided that is easy 4. visible locations at approximately 3.5-meter intervals. Insulation Mineral Wool 1. Mineral pipe insulation sections shall have a nominal density of not less than 120 kg/m³. Pre-formed pipe sections shall be resin bonded with a thermal conductivity not exceeding 0.038 W/mK at 50 °C me an temperature 2. Mineral wool duct slab shall have a nominal density of not less than 45kg/m³ with a thermal conductivity not exceeding 0.04 W/mK at 50 °C mean temperature. 3. Thickness of insulation shall be in accordance with BS 5422: 2001

## Table 98
Piping Works Valves, cocks, air vents and pipework accessories shall be provided where indicated on the drawings and at all positions necessary for the proper working, regulation, control and maintenance of the installation with the approval. Double regulating Valve Fixed orifice double regulating valve to BS7350 Valve body material: Bronze Pressure rating: PN25 End connections: Threaded to BS 21 Specification: Fitted with two insertion points allowing quick connection.

## Table 99
Approved Manufacturers / Vendors ;

## Table 100
Sr.No | Material Description | Make
HVAC
1 | Heater Batteries | Bissol or equivalent
2 | Duct Sensors & Thermostat | Honeywell
3 | Galvanized Iron ( GI) Duct | Nippon -Japan, Or equivalent
4 | Mineral Wool Insulation | Rock Wool -Fujairah
5 | Volume Control Dampers | Local
6 | MS Piping for Heater Battery | Suriya
7 | MI Fitting for LTHW | Crane
8 | Heater battery Valves Assembly | Crane
9 | Flexible Duct | Supaflex or equivalent
10 | Flexible Duct Rigid | Supaflex or equivalent
11 | Disc Valves | Betacad
12 | Air Diffusers | Betecad
13 | Angle/Support/Nut/Rods | N/A
14 | Control valve | ACSYS Control
15 | Thermostat Make - Alerton (Honeywell) Model - VLD-362-FF | BMTS
Sanitory/Plumbing
1 | Wash Basin | RAK-Karla

## Table 102
2 | Wash Basin – Mixer Auto | RAK-Kludi - Zentia
3 | Floor Drain Cover | Generic
4 | Acrylic Sheet wall protection 3 mm thick white Milky | Generic
5 | Bottle Trap with Waste | Vigga – CP
6 | Domestic Water Supply PPR Pipe | Aquatherm- Germany
7 | Soil & Waste Drainage PVC Grey | Hepworth Cory
Fire Fighting
1 | Pendant Sprinkler Head NPT Thread K-5.6, 79C Standard response Bronze finish UL /FM ( RA3415) Make Reliable Model F156 | Al Arabia
2 | Concealed Pendent Sprinkler Head NPT Thread K-5.6, 74C Quick response White cover plate finish UL /FM ( RA3415) Make Reliable Model G5-56 | Al Arabia
3 | GI Piping | Suriya Schedule 40
4 | GI Fitting | SIAM -Thailand.
Medical Gas System
1 | Bedhead Units | Dorsys-UAE
2 | Copper Piping | Lawton-UK
3 | Lockable Line Valves | Medical Grade
4 | Medical Gas Valves | Medical Grade
5 | Area Service Unit c/w Alarm | Beacon Medas or equivalent as per approved sample
Electrical & Low Current
1 | 2 Gang DP With Red R/R | MK
2 | 2 Gang DP With Neon | MK
3 | 1 Gang DP With Neon | MK
4 | 1 Gang DP With Red R/R | MK
5 | GI Box 3 x 6 Make | MK
6 | GI Box 3 x 3 Make | MK
7 | GI Box 3 x 3 Deep Make | MK
8 | 6 Gang Grid Switch | MK
9 | 1 Gang 1 Way Switch W/R | MK
10 | 2 Gang 1 Way Switch W/R | MK
11 | 3 Gang 1 Way Switch W/R | MK
12 | Telephone Data outlet | Schneider
13 | RJ 45 Key Stone Jack | Schneider
14 | RJ 45 Jack | Schneider
15 | Patch Panel 24 Port | Schneider
16 | Sub Circuit Monitor (CBS) | Eaton
17 | SVAEL Unit (CBS) | Eaton
18 | Exit Light Wall Mounted | Eaton
19 | Exit Light Hanging Type | Eaton
20 | LED Panel 60 x 60 36W | Ledvance specialized services
21 | LED Down Light | Ledvance
22 | LED Spotlight | Ledvance
23 | Card Reader HID RP 40 | HID
24 | Magnetic Lock | Generic
25 | Push Button | Generic

## Table 104
26 | Belden Cable | Belden
27 | Cable Cat6 UTP | Schneider
28 | FP 200 Wire - White & RED | Ducab
29 | Flexible Wire | Ducab
30 | Wire – Single Core | Ducab
31 | GI Trunking Fitting HDG ( Hot Dipped Galvanized) | Unitech-UAE
32 | Earth Strip | Unitech-UAE
33 | PVC Conduit | Decduct
34 | PVC Conduit Accessories | Decduct
35 | PVC Connector | Generic
36 | PVC Conduit fittings | Decoduct
37 | Kopex Gland Complete | Barton
38 | GI Flexible Conduit | Barton
39 | Kopex Gland | Copex
40 | PVC circular Junction Box , Saddel, and Cover | Decoduct
41 | SD/MCP/PROG | GE-USA
42 | ELCB | ABB
43 | MCB | ABB
44 | Cable - XLPE | Ducab
45 | Cable - ECC | Ducab
46 | Cable Gland | Bicon
47 | E- Fiercely | Generic

## Table 105
GROSS 3057 | HISTOPATHOLOGY & CYTOPATHOLOGY | RM-01 1 BED | RM-02 1 BED | DIRTY UT RM 4331 | HSKP. 2321 | STAIR NO. 6 DN

## Table 106
CHEMICAL STORAGE 3269 | WC 6071 | 6000 | FHR WC | 10066 RM-05 1 BED

## Table 107
STORAGE 3246 | 8625 | 5695 | 6026 | 2400

## Table 108
ICROSCOPY ROOM 3295 | TESTING MICROSCOPE 3295 | 1800 | DOCTOR OFFICE 3282 | CONSOLE WC | 2604 HIDDEN DOOR | 2933 HIDDEN DOOR | CONSOLE WC | RM-06 WC 1 BED

## Table 109
5014 MANAGER OFFICE | DOCTOR OFFICE | PREMIUM RM-03 1 BED | PREMIUM RM-04 1 BED | WC RM-07 1 BED

## Table 110
DOCTOR OFFICE

## Table 111
DOCTOR OFFICE 5014 LOUNGE | 3072 | SECRETARY | MEETING / STAFF RM. 3281 | STAFF LOCKER 4132 STAFF PANTRY | 1500 | DOCTOR OFFICE 3220 DOCTOR OFFICE | 2562 CLEAN UT RM MED.WASTE RM | RM-08 WC 1 BED WC RM-09 1 BED

## Table 112
2789 | COMM. 5620 | ELEC. 4477 | 1500 | MEDICATION PREP RM 4200 | 9267

## Table 113
F/WC | M/WC | NURSE STATION

## Table 114
RM-10 WC 1 BED

## Table 115
LOBBY | 2400 | MEETING RM 2713 | STORE 2500 | 5762 BABY OBSERVATION RM | 2000 | WC 2000 | RM-11 1 BED 6667

## Table 116
2769 | LOUNGE | BRIDGE CORRIDOR TO EXPANSION | Automatic Sliding Door

## Table 117
FFICE 21 | 1-5134 COR. 1-5134 | F.TOILET 1-5084 M.TOILET 1-5087 | MEETING RM | Automatic Sliding Door 1182 | 866 | 7000 WC RM-12 1 BED | 2400 | WC ANTE | ISOLATION RM-14

## Table 118
1-5135 | WC 2159 | WC 2174 | RM-13 WC 1 BED | 7400 RM-15 1 BED

## Table 119
TRACTION 1-5120 | COR. WC 1-5135

## Table 120
MEDICAL DIRECTOR RM 4322 | NURSING DIRECTOR RM 4321 | 6050 | 1036

## Table 121
-5122B | 1-5123B | RECEPTION 1-5119 | 1-5128B | 1-5129B | EQUIPMENT STORE RM | NURSE STATION | 2423 | PREMIUM RM-16 1 BED

## Table 122
TREATMENT TREATMENT TREATMENT | TREATMENT | CUBICLE-1 | CUBICLE-2 | CUBICLE-3 | FEMALE SHOWER 1-5086

## Table 123
6 122 -51ME22NAT | TREATMENT 5 1-5123 1-5123A | 4 1-5124 1-5124 | 3 1-5125 1-5125 | 2 1-5128 1-5128A | 1 1-5129 1-5129A | 1-5130B | CUBICLE-4 | CUBICLE-5 | CUBICLE-6 | 1-5086 | WC PANTRY

## Table 124
FEMALE GYM 1-5130 | FEMALE TREATMENT 1-5130 | STAIR NO. 7 DN

## Table 125
LACTATION OFFICE

## Table 126
4083